## Slide 1: Actuators and Control

## Slide 2: control devıces
This section deals with control devices used for regulating temperature, pressure, controlling liquid, and gas flow in industrial processing.
The devices can be self-regulating or under the control of a central processing system that can be monitoring and controlling many variables.
This section will discuss actuators and regulators and their use for the control of gas flow, liquid flow, and pressure control.

## Slide 3: Regulators
Gases used in industrial processing, such as oxygen, nitrogen, hydrogen, and propane, are stored in high-pressure containers in liquid form.
The high-pressure gases from above the liquid are reduced in pressure and regulated with gas regulators to a lower pounds per square inch before they can be distributed through the facility.
The gas lines may have additional regulators at the point of use.

## Slide 4: Pressure Controllers
A spring-controlled regulator is an internally controlled pressure regulator and is shown in Figure. Initially, the spring holds the inlet valve open and gas under pressure flows into the main cylinder at a rate higher than it can exit the cylinder. As the pressure in the cylinder increases, a predetermined pressure is reached where the spring loaded diaphragm starts to move up, causing the valve to partially close, i.e., the pressure on the diaphragm controls the flow of gas into the cylinder to maintain a constant pressure in the main cylinder and at the output, regardless of the flow rate (ideally). The output pressure can be adjusted by the spring screw adjustment.

## Slide 5: Pressure Controllers
A weight-controlled regulator is shown in Figure.
The internally controlled regulator has a weight-loaded diaphragm.
The operation is the same as the spring-loaded diaphragm except the spring is replaced with a weight.
The pressure can be adjusted by the position of a sliding weight on a cantilever arm.

## Slide 6: pressure-controlled dıaphragm regulator
A pressure-controlled diaphragm regulator is shown in Figure. The internally controlled regulator has a pressure-loaded diaphragm.
Pressure from a regulated external air or gas supply is used to load the diaphragm via a restriction.
The pressure to the regulator can then be adjusted by an adjustable bleed valve, which in turn is used to set the output pressure of the regulator.

## Slide 7: Externally connected sprıng dıaphragm regulator
Externally connected spring diaphragm regulator is shown in Figure.
The cross section shows an externally connected spring-loaded pressure regulator.
The spring holds the valve open until the output pressure, which is fed to the upper surface of the diaphragm, overcomes the force of the spring on the diaphragm, and starts to close the valve, hence regulating the output pressure.
Note that the valve is inverted from the internal regulator and the internal pressure is isolated from the lower side of the diaphragm.
Weight- and air-loaded diaphragms are also available for externally connected regulators.

## Slide 8: Pılot-operated pressure regulators
Pilot-operated pressure regulators can use an internal or external pilot for feedback signal amplification and control.
The pilot is a small regulator positioned between the pressure connection to the regulator and the loading pressure on the diaphragm. Figure shows such an externally connected pilot regulator.
The pressure from the output of the regulator is used to control the pilot, which in turn amplifies the signal and controls the pressure from the air supply to the diaphragm, giving greater control than that available with the internal pressure control diaphragm.
A slight change in the output pressure is required to produce a full pressure range change of the regulator giving a high gain system for good output pressure regulation.
An Instrument pilot-operated pressure regulator is similar to the pilot-operated pressure regulator but has a proportional band adjustment included, giving a gain or sensitivity control feature to provide greater flexibility in control.

## Slide 9: Safety valves
Safety valves are fitted to all high-pressure containers from steam generators to domestic water heaters.
The valve is closed until the pressure on the lower face of the valve reaches a predetermined level set by the spring.
When this level is reached, the valve moves up allowing the excess pressure to escape through the vent.

## Slide 10: Level regulators
Level regulators are in common use in industry to maintain a constant fluid pressure, or a constant fluid supply to a process, or in waste storage.
Level regulators can be a simple float and valve arrangement as shown in Figure. The arrangement shown in Figure is used to control water levels in many applications.
When the fluid level drops due to use, the float moves downward opening the inlet valve and allowing fluid to flow into the tank.
As the tank fills, the float rises, causing the inlet valve to close, thus maintaining a constant level and preventing the tank from overflowing.

## Slide 11: Level regulators
Figure shows an example of a self-emptying reservoir when a predetermined fluid level is reached, as may be used in a waste holding tank.
As the tank fills, the float rises to where the connecting link from the float to the valve becomes taut and overcomes the hydrostatic pressure on and lifting the outlet valve.
Once lifted, the fluid pressure under the valve balances the pressure above the valve and the buoyancy of the valve will keep it open until the tank is empty, then it will close. Once closed the reservoir will start to fill and the fluid pressure on the top surface of the valve will hold it closed.

## Slide 12: Level regulators
The position of the weight in Figure is controlled by the float. The position of the weight is monitored by position sensors A and B.
When the weight is in position A (container empty), the sensor can be used to turn on a pump to fill the tank and when sensor B senses the weight (container full) it can be used to turn the pump off.
The weight can be made of a magnetic material and the level sensors would be Hall effect or magneto resistive element (MRE) devices.
DR. KADRİYE ÖZLEM HAMALOĞLU
17.12.2018

## Slide 13: Flow Control Actuators
When a change in a measured variable with respect to a reference has been sensed , it is necessary to apply a control signal to an actuator to make corrections to an input controlled variable to bring the measured variable back to its preset value.
In most cases any change in the variables, i.e., temperature, pressure, mixing ingredients, and level, can be corrected by controlling flow rates.
Hence, actuators are in general used for flow rate control and can be electrically, pneumatically, or hydraulically controlled.
Actuators can be self-operating in local feedback loops in such applications as temperature sensing with direct hydraulic or pneumatic valve control, pressure regulators, and float level controllers.
There are two common types of variable aperture actuators used for flow control; they are the globe valve and the butterfly valve.

## Slide 14: Globe valve
The globe valve’s cross section is shown in Figure.
The actuator can be driven electrically using a solenoid or motor, pneumatically or hydraulically.
The actuator determines the speed of travel and distance the valve shaft travels.
The globe type valve can be designed for quick opening, linear, or equal percentage operation.
In equal percentage operation the flow is proportional to the percentage the valve is open, or there is a log relationship between the flow and valve travel.
The shape of the plug determines the flow characteristics of the actuator and is normally described in terms of percentage of flow versus percentage of lift or travel.
The valve plug shown in Figure gives a linear relationship between flow and lift.

## Slide 15: Globe valve characterıstıc
The characteristic is given in Figure.
Also shown in the graph are the characteristics for a quick opening plug and an equal percentage plug to illustrate some of the characteristics that can be obtained from the large number of plugs that are available.
The selection of the type of control plug should be carefully chosen for any particular application.
The type will depend on a careful analysis of the process characteristics, i.e., if the load changes are linear a linear plug should be used. Conversely, if the load changes are nonlinear a plug with the appropriate nonlinear characteristic should be used.

## Slide 16: Globe valve confıguratıons
The globe valve can be straight through with single seating as illustrated in Figure or can be configured with double seating, which is used to reduce the actuator operating force, but is expensive, difficult to adjust and maintain, and does not have a tight seal when shutoff.
Angle valves are also available, i.e., the output port is at right angles or 45° to the input port.
Many other configurations of the globe valve are available. Illustrated in Figure is a two-way valve (diverging type), which is used to switch theincoming flow from one exit to another. When the valve stem is up the lower port is closed and the incoming liquid exits to the right, and when the valve is down the upper port is closed and the liquid exits from the bottom.

## Slide 17: Three-way valve
Figure illustrates a three-way valve. In the neutral position both exit ports are held closed by the spring. When the valve stem moves down the top port is opened and when the valve stem moves up from the neutral position the lower port is opened.
Other types of globe valves are the needle valve (less than 1-in diameter), the balanced cage-guided valve, and the split body valve. In the cage-guided valve, the plug is grooved to balance the pressure in the valve body.
The valve has good sealing when shut off. The split body valve is designed for ease of maintenance and can be more cost effective than the standard globe valve, but pipe stresses can be transmitted to the valve and cause it to leak.
Globe valves are not well suited for use with slurries.

## Slide 18: Butterfly valve
The butterfly valve is shown in Figure and its flow versus travel characteristics are shown in Figure below.
The relation between flow and lift is approximately equal percentage up to about 50 percent open, after which it is linear.
Butterfly valves offer high capacity at low cost, are simple in design, easy to install, and have tight closure.
The torsion force on the shaft increases until open up to 70° and then reverses.

## Slide 19: Other valve types
A number of other types of valves are in common use. They are the weir diaphragm, ball, and rotary plug valves. The cross sections of these valves are shown in Figure.

## Slide 20: weır-type dıaphragm
A weir-type diaphragm valve is shown in Figure.
The valve is shown open; closure is achieved by forcing a flexible membrane down onto the weir.
Diaphragm valves are good for slurries and liquids with suspended solids, are low cost devices, but tend to require high maintenance, and have poor flow characteristics.

## Slide 21: one-pıece ball valve
A one-piece ball valve is shown in Figure.
The valve is a partial sphere that rotates.
The valve tends to be slow to open.
Other than the one shown in the figure, the ball valve is available in other configurations also with spheres of various shapes for different flow characteristics.
The valve is good for slurries and liquids with solid matter because of its self-cleaning operation.
Ball valves have tight turnoff characteristics, are simple in design, and have greater capacity than similar-sized globe valves.

## Slide 22: eccentrıc rotary plug valve
An eccentric rotary plug valve is shown in Figure.
The valve is of medium cost but requires less closing force than many valves and can be used for forward or reverse flow.
The valve has tight shutoff with positive seating action, has high capacity, and can be used with corrosive liquids

## Slide 23: Valve characterıstıcs
Other factors that determine the choice of valve type are corrosion resistance, operating temperature ranges, high and low pressures, velocities, and fluids containing solids.
Correct valve installation is essential; vendor recommendations must be carefully followed.
In situations where sludge or solid particulates can be trapped upstream of a valve, a means of purging the pipe must be available.

## Slide 24: Valve characterıstıcs